## Equipment Info
EQUIPMENT PERFORMANCE — CONDITION MONITORING RECORD
NAMEPLATE / IDENTIFICATION |  | MONITORED PARAMETERS & LIMITS
Equipment Tag | PM-4405B | Parameter | Alarm / Trip
Equipment Name | Cooling Water Pump PM-4405B (Motor Driven) | Motor DE Bearing Temp (°C) | 75 / 90
Equipment Type | Centrifugal Pump / Electric Motor | Motor Vibration (mm/s) | 5.0 / 8.0
Equipment Class | B | Motor Ampere (A) | 150 / 165
Plant / Unit | Utility Plant (NUP) | Winding Temp (°C) | 120 / 140
Discipline | ELE
Criticality | Medium
Design Life | 5 years (bearing) / 24 months (seal element)
Monitoring Method | Online DCS + monthly vibration/thermography route
Linked RCA / AR No. | AR-2026-NUP-0089
Failure Date | 08-Jul-2026
Dominant Failure Mode | Motor Bearing Failure (Overheating)

## Condition History
Week | Date | Motor DE Bearing Temp (°C) | Motor Vibration (mm/s) | Motor Ampere (A) | Winding Temp (°C) | Health Status | Remark
1 | 2026-02-18 | 63.617 | 2.468 | 133.725 | 96.639 | NORMAL
2 | 2026-02-25 | 64.04 | 2.443 | 131.366 | 94.458 | NORMAL
3 | 2026-03-04 | 64.006 | 2.679 | 132.215 | 96.07 | NORMAL
4 | 2026-03-11 | 64.94 | 2.618 | 132.454 | 96.361 | NORMAL
5 | 2026-03-18 | 65.55 | 2.782 | 134.231 | 95.593 | NORMAL
6 | 2026-03-25 | 65.645 | 3.003 | 133.577 | 96.823 | NORMAL
7 | 2026-04-01 | 66.476 | 3.062 | 134.033 | 98.95 | NORMAL
8 | 2026-04-08 | 66.851 | 3.201 | 134.385 | 99.369 | NORMAL
9 | 2026-04-15 | 68.559 | 3.343 | 136.254 | 100.744 | NORMAL
10 | 2026-04-22 | 69.633 | 3.706 | 138.69 | 103.699 | NORMAL
11 | 2026-04-29 | 70.413 | 4.2 | 139.701 | 104.721 | NORMAL
12 | 2026-05-06 | 71.385 | 4.132 | 142.763 | 108.321 | NORMAL
13 | 2026-05-13 | 73.921 | 4.388 | 142.827 | 110.606 | NORMAL
14 | 2026-05-20 | 74.537 | 4.838 | 145.824 | 114.327 | NORMAL
15 | 2026-05-27 | 76.498 | 5.375 | 147.179 | 117.834 | ALARM
16 | 2026-06-03 | 78.258 | 5.606 | 150.389 | 118.576 | ALARM
17 | 2026-06-10 | 80.814 | 6.043 | 152.555 | 123.3 | ALARM
18 | 2026-06-17 | 82.788 | 6.493 | 155.447 | 128.027 | ALARM | Degradation trend — under close monitoring
19 | 2026-06-24 | 84.415 | 6.991 | 157.396 | 133.654 | ALARM | Degradation trend — under close monitoring
20 | 2026-07-01 | 87.236 | 7.372 | 162.307 | 135.486 | ALARM | Degradation trend — under close monitoring
21 | 2026-07-08 | 91.8 | 8.16 | 168.3 | 142.8 | TRIP | FAILURE — Motor Bearing Failure (Overheating); unplanned downtime 8.0 h
22 | 2026-07-15 | 63.965 | 2.545 | 127.659 | 91.57 | NORMAL | Post-repair baseline restored (CAPA executed)
23 | 2026-07-22 | 65.846 | 2.681 | 127.446 | 97.367 | NORMAL
24 | 2026-07-29 | 64.984 | 2.428 | 127.592 | 92.001 | NORMAL
25 | 2026-08-05 | 65.038 | 2.529 | 132.291 | 93.757 | NORMAL
26 | 2026-08-12 | 64.849 | 2.528 | 131.854 | 94.427 | NORMAL

## Performance Summary
PERFORMANCE SUMMARY — PM-4405B
KPI | Value | Basis / Formula
Monitoring Period (weeks) | 26 | Number of weekly readings
Total Downtime (hours) | 8 | From linked RCA downtime window
Period Hours | 4368 | 4368
Availability (%) | 99.8168 | (Period-Downtime)/Period
No. of Failures (period) | 1 | Failure events this period
MTBF (hours) | 4368 | Period Hours / No. of Failures
MTTR (hours) | 8 | Mean time to repair
ALARM readings | 6 | Count of ALARM weeks
TRIP readings | 1 | Count of TRIP weeks
NORMAL readings | 19 | Count of NORMAL weeks
PM Compliance (%) | 92 | PM completed vs scheduled
Production Loss (ton) | 160 | Downtime x rate loss (from RCA)
Estimated Loss (k USD) | 112 | Production loss x product price