## Slide 1
ABNORMALITY REPORT — RCA & CAPA/PAA
Equipment Related Risk
Cooling Water Pump PM-4405B (Motor Driven)
Motor Bearing Failure (Overheating)
AR NUMBER
AR-2026-NUP-0089
TAG / PLANT
PM-4405B | NUP
DATE OCCURRENCE
08 Jul 2026
PRE-RISK
III (Score 200)
PIC (RCA)
REL-02
Procedure No. RCA-P-0050-03 • Form RCA-F-0075-02

## Slide 2
PROBLEM IDENTIFICATION
AR Details & Problem Statement
02/11
AR IDENTIFICATION
Title / Problem
Cooling Water Pump PM-4405B (Motor Driven) — Motor Bearing Failure (Overheating)
AR Type
OPEDR (Operation) — Uptime
Plant / Unit
NUP (Nova Utility Plant)
Tag / Eq. Class
PM-4405B | Class B
Discipline
ELE
Date Occurrence
08 Jul 2026
Date Reported
08 Jul 2026
Immediate Action
Start standby CW pump PM-4405C, isolate PM-4405B, replace motor DE & NDE bearings
SEVERITY
Moderate
PRE-RISK
III
DOWNTIME
8.0 h
LOSS
$112.0k
PROBLEM STATEMENT
Cooling Water Pump PM-4405B motor tripped on 08-Jul-2026 due to drive-end bearing failure from grease degradation and an over-extended re-lubrication interval.
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 3
GENERAL PROCESS OVERVIEW
Chronology of Events
03/11
06-Jul-2026
Cooling-water system running on PM-4405B; motor DE bearing temperature trending up (68 → 84 °C).
08-Jul-2026 13:20
Motor bearing high-temperature alarm; motor tripped on winding/bearing over-temp.
08-Jul-2026 13:35
Standby PM-4405C started; cooling-water supply maintained at reduced margin.
08-Jul-2026 16:00
Motor DE bearing found seized; grease degraded/carbonized. NDE bearing marginal.
08-Jul-2026 21:20
DE & NDE bearings replaced and re-greased; motor recommissioned.
Problem: Cooling Water Pump PM-4405B motor tripped on 08-Jul-2026 due to drive-end bearing failure from grease degradation and an over-extended re-lubrication interval.
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 4
ASSESS
Past Performance Analysis
04/11
HISTORICAL DATA & EVIDENCE
PM-4405B motor bearing temperature baseline is 60–68 °C. Re-lubrication was performed on a fixed 12-month interval regardless of duty/ambient. Bearing temperature was not trended in CMMS, so degradation went unnoticed.
IMPACT SUMMARY (4W)
What:
PM-4405B motor DE bearing failed / overheated
When:
08-Jul-2026 (13:20)
Scope:
Loss of one cooling-water pump; reduced CW margin (standby covered)
Uptime Loss:
8.0 hours → 160.0 ton → $112.0k
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 5
TARGET SETTING
Actual vs Target Condition
05/11
ACTUAL CONDITION (Before Improvement)
CW pump motor trip due to bearing overheating
TARGET CONDITION (Project Y)
No motor bearing failure due to lubrication (bearing temp < 75 °C, risk-based re-greasing)
TARGET METRIC
Recurrence of this equipment failure mode:
Before = 1 case → Target = 0 case
Chart: Failure Case — Before vs Target
| Before | Target
Failure Cases | 1 | 0
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 6
ROOT CAUSE ANALYSIS
Parameter Verification (4P)
06/11
#
Problem Phenomenon / Parameter
Result
Evidence / Finding
P1
Motor bearing temperature above limit
NG
DE bearing reached 84 °C vs 75 °C alarm — grease breakdown.
P2
Motor over-loaded (high ampere)
G
Running current 132 A vs 150 A rated — within limit.
P3
Cooling-fan / ventilation blocked
G
Fan cowl clean; ambient ventilation adequate.
P4
Grease type incorrect
G
Correct high-temp lithium-complex grease used.
P5
Bearing beyond service life
G
Bearing in service 2 years vs 5-year design — within life.
NG = current condition not meeting standard (problem) • G = meets standard
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 7
ROOT CAUSE ANALYSIS
4M + 1E Verification
07/11
#
Man / Machine / Method / Material / Environment
Result
Evidence / Finding
X1
Re-lubrication interval not risk-based
NG
Fixed 12-month interval too long for duty & ambient — grease degraded.
X2
Bearing temperature not trended in CMMS
NG
No condition-based trigger; only alarm at failure point.
X3
Vibration route excludes utility motors
NG
PM-4405B not on the monthly vibration route.
X4
Operator round frequency
G
Rounds performed per schedule; local gauge read.
ROOT CAUSE: Motor drive-end bearing failure caused by grease degradation from an over-extended, non-risk-based re-lubrication interval, undetected due to absence of bearing-temperature trending, resulting in bearing overheating and motor trip.
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 8
RCA — MATRIX PRIORITY
Impact vs Control Prioritization
08/11
X1 X2 X3
P1
Low
Medium
High
IMPACT →
CONTROL →
Low
Medium
High
Prioritized root causes (high impact) are addressed first via Corrective & Pro-Active Actions →
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 9
IMPROVE
Corrective & Pro-Active Action (CAPAA)
09/11
RC
Corrective Action
Plan Date
PIC
Status
X1
Revise PM-4405B re-lubrication interval to risk-based (4-monthly)
31-Jul-2026
REL-02
In Progress
X2
Add motor bearing temperature trending & alert to CMMS
31-Aug-2026
REL-05
Open
PRO-ACTIVE ACTION (roll-out to similar equipment)
RC
Pro-Active Action
Plan Date
PIC
Status
X1
Apply risk-based re-greasing to all CW pump motors
31-Aug-2026
REL-02
Open
X2
Extend bearing-temp trending to utility motor fleet
30-Sep-2026
REL-05
Open
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 10
IMPROVE
Preventive & Risk Analysis
10/11
PREVENTIVE / PRO-ACTIVE ACTION (Good Condition Parameters)
Item
Possible Root Cause
Preventive Action
Plan Date
PIC
X3
Motor not on vibration route
Add PM-4405B/C to monthly vibration & thermography route
31-Jul-2026
REL-02
P1
Bearing over-temp
Verify motor cooling-fan & louvre condition each PM
31-Jul-2026
ELE-01
RISK ANALYSIS OF CORRECTIVE ACTION
Corrective Action
Potential Risk
Countermeasure
Plan Date
PIC
Shorten re-greasing interval
Over-greasing risk (churning / seal push-out)
Use metered re-greasing per bearing volume calc
31-Jul-2026
REL-02
PM SCHEDULE ESTABLISHED
PM No.
Description
Group
Interval
PM-1
Risk-based motor bearing re-greasing PM-4405B
Electrical
4-monthly
PM-2
Monthly motor bearing temperature & vibration reading
Reliability
Monthly
RCA & CAPA/PAA | AR-2026-NUP-0089 | PM-4405B — NUP

## Slide 11
Downtime & Closure Summary
DOWNTIME
8.0 h
PRODUCTION LOSS
160.0 ton
ESTIMATED LOSS
$112.0k
PRE-RISK
III (200)
ROOT CAUSE
Motor drive-end bearing failure caused by grease degradation from an over-extended, non-risk-based re-lubrication interval, undetected due to absence of bearing-temperature trending, resulting in bearing overheating and motor trip.
KEY CORRECTIVE / PRO-ACTIVE ACTIONS
• Revise PM-4405B re-lubrication interval to risk-based (4-monthly)
• Add motor bearing temperature trending & alert to CMMS
• Add PM-4405B/C to monthly vibration & thermography route
AR-2026-NUP-0089 • PM-4405B — NUP